# Design program for Power Factor Correction and Load Analysis

Solomon Ofori Manu, Graduate ECE Student University of Alabama at Birmingham, Student Member, IEEE

Abstract: In today's energy-conscious world with economic downturns, optimizing the efficiency of electrical systems is of paramount importance. Power factor correction is a critical aspect of electrical power systems that aims to improve the efficiency and optimization of electrical power distribution by adjusting the phase relationship between voltage and current. This report introduces a program designed to curb power factor correction problems efficiently. The program takes user inputs pertaining to the electrical system, source voltage, number of loads, and desired power factor correction with its parameters, active power, apparent power, reactive power and the phase angle as well as provides the required capacitor bank sizes for both single-phase and three-phase systems for both Wye and Delta connections.

Index Terms

- Impedance (Z)

- Current magnitude (I)

- Voltage(V)

- Angle (phi) in degrees

- Apparent power (S)

- Real power (P)

- Reactive power (Q)

- Power factor (pf)

.

# design philosophy

Electrical power is a fundamental resource in modern society, and its efficient utilization is paramount for various applications, ranging from industrial facilities to residential buildings. One critical aspect of efficient power utilization is power factor correction. Power factor correction involves the adjustment of reactive power components in electrical systems to improve power factor, reduce losses, and enhance energy efficiency.

The optimal power factor is unity or represented as one. Anything lower than one implies that additional power is necessary to accomplish the intended work. Current flow, in any case, leads to inefficiencies, resulting in losses within the power supply and distribution systems. A load operating with a power factor of 1.0 signifies the most efficient utilization of the power supply. Conversely, a load with a power factor, for instance, of 0.8, leads to considerably greater losses within the supply system and a larger utility bill for the consumer. Even a relatively modest enhancement in the power factor can yield a noteworthy reduction in losses, given that these losses increase proportionally to the square of the current.

A low power factor typically arises from inductive loads like induction motors or power transformers. It generally occurs when there is a substantial phase disparity between the voltage and current at the load terminals. Alternatively, it can be attributed to a high presence of harmonics or an irregular current waveform. Power factor degradation stemming from inductive loads can be rectified through the incorporation of power factor correction devices.

In Summary, Power factor is a measurement of how efficiently a facility uses electrical energy. A high power factor means that electrical power is being utilized effectively, while a low power factor indicates poor utilization of electric power. Low power factor can cause equipment overloads, low voltage conditions, and greater line losses. Most importantly, low power factor can increase total demand charges and cost per kWh, resulting in higher monthly electric bills.

Low power factor is generally solved by adding power factor correction capacitors to a facility’s electrical distribution system. Power factor correction capacitors supply the necessary reactive portion of power (kVAr) for inductive devices. The principal benefit is lower monthly electric bills.

The "Power Factor Correction and Load Analysis Program" is a MATLAB-based tool developed to analyze and optimize electrical loads in both single-phase and three-phase systems. It offers functionalities to calculate critical electrical parameters such as impedance(Z), current(I), angle(φ), apparent power(S), real power(P), reactive power,(Q) and power factor(pf) for various load types. Furthermore, the program provides a capability for power factor correction, allowing users to improve system efficiency by adjusting power factor.

Features

- System Data Input:

The program starts by asking the user to input some system data:

System type (single-phase or three-phase)

Source voltage (V)

- Load Details Input:

The program asks the user to input details for each load in the system: Load type (S & pf, P & pf, P+jQ, R+jX - Parallel, R+jX - Series) and then number of loads.

Depending on the load type, the user is prompted to input relevant parameters, such as apparent power (S), real power (P), reactive power (Q), resistance (R), reactance (X), and more.

- Display Original Load Parameters:

The program displays the calculated parameters for each load and the total load parameters, including impedance, current, angle, apparent power, real power, reactive power, and power factor.

- New Load Parameter Calculations:

The program calculates new load parameters to achieve the desired power factor:

Angle (phi_target) in degrees is calculated from the desired power factor using inverse cosine.

New apparent power (new_total_S) is calculated based on the desired real power (total_P) and desired power factor (pf_target).

New reactive power (new_total_Q) is calculated using the new apparent power and total real power.

- Required Capacitor Bank Size Calculation:

The program calculates the required capacitor bank size to correct the power factor:

Change in reactive power (delta_Q) is calculated as the difference between the original total reactive power (total_Q) and the new total reactive power (new_total_Q).

Change in the tangent of the angle (delta_phi) is calculated as the difference between the original angle (phi_deg) and the desired angle (phi_target).

Capacitive ohms (capacitive_ohms) are calculated based on Voltage  and delta_Q.

Capacitance in farads (capacitance_farads) is calculated for both single-phase and three-phase systems, depending on the user's choice in both wye and delta connections.

- Display Comparison of Original and New Load Parameters:

The program displays a comparison of the original and new load parameters, including impedance, current, angle, apparent power, real power, reactive power, and power factor.

# DETAILED DESIGN EQUATIONS

In this section, the program begins by prompting the user to input the type of electrical system, either "single-phase" or "three-phase," followed by the source voltage (V). Subsequently, the user is asked to specify the load type (e.g., S & pf, P & pf, P+jQ, R+jX - Parallel, R+jX - Series) and the number of loads in the system. The program then calculates key electrical parameters for each load based on the specified load type. Find below the Load Calculation for each type.

## S & pf Load Type

- Calculate impedance Z based on apparent power S, Voltage V and power factor pf.

Z=SV* cos-1pf

- Compute current IL magnitude using the apparent power S and voltage VL.

I = S3 *  V

- Compute angle(∅) in degrees

φ= cos-1pf

- Determine real power P and reactive power Q using apparent power S and power factor pf.

P=S*pf

Q= S2- P2

## P & pf Load Type

- Calculate apparent power S based on real power P and power factor pf.

S=P*pf

- Compute reactive power Q using apparent power S and power factor pf.

Q= S2- P2

- Determine impedance Z using real power P and voltage V.

Z=  V2P

- Compute angle(∅) in degrees

φ= cos-1pf

## P+jQ Load Type

- Calculate apparent power S based on real power P and reactive power Q.

S= P2+ Q2

- Determine impedance Z using apparent power S and voltage V

Z=  V2S

- Compute current I magnitude using the apparent power S and voltage V.

I= SV

- Compute pf using apparent S and real power P.

pf=  PS

- Compute angle(φ) in degrees

φ= cos-1pf

## R+jX - Parallel Load Type

- Calculate impedance Z for a load with resistance R and reactance X in parallel Units.

Z= 11R +  1X

- Compute current I magnitude using the apparent power S and voltage V.

I= VZ

- Compute angle(φ) in degrees

φ= tan-1X-1R-1

- Compute pf using angle(φ)

pf=cosφ

- Compute apparent S using Current I and Voltage V

S=  I*V

- Compute real power P and reactive power Q

P=V*I cosφ

Q=V*I sinφ

## R+jX - Series Load Type

- Calculate impedance Z for a load with resistance R and reactance X in Series Units.

Z=  R+jX

- Compute current I magnitude using the apparent power S and voltage V.

I= VZ

- Compute angle(φ)) in degrees

φ= tan-1XR

- Compute pf using angle(φ))

pf=cosφ)

- Compute apparent S using Current I and Voltage V

S=  I*V

- Compute real power P and reactive power Q

P=  I*V cosφ)

Q=  I*V sinφ)

## Calculation required capacitor bank size for power factor pf correction.

## Desired Power Factor pf is given and the following calculations are done to get the target angle∅(phi_target ), new_total apparent power S and new_ total Reactive Power Q whiles real power P remains same. The required capacitive ohms and capacitive reactance is calculated.

- Compute phi_target angle(φ)) in degrees

φ)desired= cos-1pfdesired

- Compute new_total apparent Power Snew

Snew= Ppfdesired

- Compute new_total Reactive Power Qnew

Qnew= Snew2- P2

- Calculate Delta_Q ∆Q

∆Q= Q- Qnew

- Calculate the required capacitive reactance XC ( in ohms)

XC= V2∆Q

- Calculate the required capacitive reactance C ( in farads)

C= ∆QV2* ω

## Calculation required capacitor bank size for current correction.

- Compute the apparent power Snew and power factor  pf

Snew= 3*V* Idesired

- Compute phi_target angle(φ)) in degrees

φ)desired= cos-1pfdesired

- Compute new_total Reactive Power Qnew

Qnew= Snew2- P2

- Calculate Delta_Q ∆Q

∆Q= Q- Qnew

- Calculate the required capacitive reactance XC ( in ohms)

XC= V2∆Q

- Calculate the required capacitive reactance C ( in farads)

C= ∆QV2* ω

# example for testing

Example 1: A distribution system is represented as the single-phase circuit shown in Figure 1.
(a) Find the apparent power S, active power P, reactive power Q and the power factor pf of the load.
(b) If a 0.95 lagging power factor is desired, what capacitance (in F) should be connected across the line to correct the power factor to the desired value.
(c) Draw the power triangles before and after power factor correction.

## Solution:
(a) R+jX - Parallel Load Type

- Calculate impedance Z for a load with resistance R and reactance X in parallel Units.

Z= 1110 +  1j4

Z=3.7139∠68.2° Ω

- Compute angle(φ) in degrees

φ= tan-14-110-1

=68.2°

- Compute current I magnitude using the Impedance Z and voltage V.

I= VZ

I= 120∠0° 3.7139∠68.2°

= 32.311∠ − 68.2° amps

- Compute apparent S using Current I and Voltage V

S=  I*V = (120∠0°)(32.311∠ − 68.2°)

=3877.3∠68.2°VA

- Compute real power P and reactive power Q

P=V*I cosφ

= 120 * 32.311 cos68.2°

P = 1440 W

Q=V*I sinφ

= 120 * 32.311 sin68.2°

Q = 3600 var

- Compute pf using angle(φ)

pf=cos68.2°

pf =  0.3714 lagging

(b) pfnew = cosφnew = 0.95 φnew = cos−1(0.95) =18.2°

Pnew = P =1440W

Snew= 14400.95

Snew =1515.8VA

Qnew= Snew2- P2

Qnew = (1515.8)2-(1440)2  = 473.3var

The reactive power provided by the capacitor bank ∆Q = Qcap = Q−Qnew = 3600−473.3 = 3126.7 var

- Calculate the required capacitive reactance XC ( in ohms)

XC= V2∆Q

XC= 12023126.7

= 4.605 Ω

- Calculate the required capacitive reactance C ( in farads)

C= ∆QV2* ω

C= 3126.71202* 377

= 5.76×10−4 F

Example 2: The one-line diagram of a three-phase power system is shown in Figure 3:

Fig. 3. One-line diagram of a three-phase power system.
(a) Find the line current with capacitor bank switch open.
(b) Calculate the capacitive ohms connected in delta that makes the line current (switch

## S & pf Load Type

(a) The line current with the switch open

- Compute current IL magnitude using the apparent power S and voltage VL.

IL = S3φ3 *  V

IL = 30 × 1063 *  34.5×103

I =502∠−53.13° A

- Compute angle(∅) in degrees

φ= cos-1pf

φ= cos-10.6

φ=53.13° A

- Compute real power P and reactive power Q

P3φ=V*I cosφ

= 34.5×103 * 502 cos68.2°

P3φ = 6 MW

Q3φ=V*I sinφ

= 34.5×103 * 502 sin68.2°

Q3φ = 8 Mvar

(b) With the switch closed, the line current (magnitude) reduced to 400 A.

- Compute the apparent power Snew and power factor  pf

Snew= 3*V* Idesired

√3(34.5×103 )(400)

= 23.902 MVA

- Compute new_total Reactive Power Qnew

Pnew = P = 6 MW

Qnew= Snew2- P2

Qnew = (23)2-(6)2  = 5.24 Mvar

The reactive power provided by the capacitor bank for delta connection;

∆Q = Qcap = Q−Qnew = 8−5.2415 = 2.785 Mvar

- Calculate the required capacitive reactance XC ( in ohms)

XC= V2∆Q

XC= 34.5×103 22.785*106

= 431.5 Ω

- Calculate the required capacitive reactance C ( in farads)

C= ∆QV2* ω

C= 2.785*106(34.5*103) 2* 377

= 6.148 ×10−6 F

# CONCLUSION

The "Power Factor Correction and Load Analysis Program" is a valuable tool for electrical engineers and professionals working on power systems. It simplifies the analysis of electrical loads and aids in optimizing power factor to enhance system efficiency. The program's ability to perform power factor correction based on user-defined parameters makes it a versatile tool for real-world applications in power system improvements.

# References

Charles A. Gross, Power System Analysis -2nd Edition,John Wiley & Sons, Wiley, 1986, p. 66-81.

E. Clarke, Circuit Analysis of AC Power Systems, vol. I.  New York: Wiley, 1950, p. 81.

IEEE Recommended Practice for Electric Power Distribution for Industrial Plants (IEEE Red Book, Std 141-1986), October 1986, IEEE, ISBN: 0471856878

IEEE Recommended Practice for Industrial and Commercial Power Systems Analysis (IEEE Brown Book, Std 399-1990), December 1990, IEEE, ISBN: 1559370440

IEEE Recommended Practice for Protection and Coordination of Industrial and Commercial Power Systems, March 1988, IEEE, ISBN: 0471853925

Industrial and Commercial Power Systems Handbook, F. S. Prabhakara, Robert L. Smith, Ray P. Stratford, November 1995, McGraw Hill Text, ISBN: 0070506248